## 6. Temska
6 – PROJECT OF MACHINE INSTALLATION
pos | description of works | unit of measure | Quantity | EUR | EUR
1 | 2 | 3 | 4 |  | 5
2 | Sanitary water preparation system
1 | Inverter air/water heat pump in a compact monobloc design for outdoor installation. With permanent monitoring of the cooling circuit, as well as optimized mode of operation according to the operating point , provided by an electronic expansion valve. Refrigerant R 32 for high SOR and flow temperatures up to 60° “S. O N.Low noise and vibration emission due to the sound-optimized design of the device with an inverter compressor.Stainless steel plate heat exchanger for the water cirrcuit. With frost protection and primary flow control.
Performance of the heat pump according to valid EU standards and guidelines, as well as valid guidelines for pressure vessels. Se E conformity.With guidance according to weather conditions, with digital regulation of the heat pump , for operation with slidingly guided water temperature. With regulation for the preparation of hot sanitary of tehnical water in one storage boiler or buffer. Integrated active cooling .Menu-driven operating unit with error display. Outside temperature sensor as well as DHW immersion sensors in the scope of delivery.
Minimum technical features and performance 1. Type of air-water heat pump 2. Nominal heat output -for oil A7/W35 according to EN 14511 dt=5k; 8,98kw 3.Energy efficiency class A+++ 4.Cooling capacity-for tauki A35/W7:6.69 KW 5. Maximum temperature of the supply line; min 60 N 6. Scopre of work in the STV preparation regime:from -20 N to 40 C 7. With integrated circulation pump 8. Heat pump expansion valve Electronic 9. Heat pump compressor :invertet double rotary
| 10. With integrated regulation of the heat control panel 11.Refrigerant:R32 12.Materialof exchanger on the water side :stainless vitocal 100-A AWO-M-AC 101.808, manufacturer viessmann Germany | piece | 1 |  | 396000
2 | Anti-vibration supports | piece | 1 |  | 120
3 | Temperature sensor | piece | 1 |  | 4700
4 | Bivalent hot water boiler with two heating pipes Vissmann Vitocell 100-B 500 lit | piece | 1 |  | 216000
5 | Modulating elecric boiler Viessmab Vitotron 100 8 kw | piece | 1 |  | 72000
6 | Delivery and installation of equipment pos.1-6 vissmapp Germany | lump sum | 1 |  | 140000
7 | Procurement, delivery and installation of an expansion vessel for sanitary water ( Sbar ) with a valume of 24liters together with a safety valve DN20 R3/4. The expansion vessel was selected based on the hydraulic calculationfrom of the VIK projekt | piece | 1 |  | 12000
8 | Procurement, delivery and installation, expansion court for heat pump installations and elecric boiler (pmax 3 bar) volume 12 liters together with safety valve DN 20 (R3/4”) | piece | 2 |  | 5000
9 | Supply,delivery and installation of poppet valves DN25 , NP6 (R1") | piece | 10 |  | 1500
10 | Supply, delivery and installation dirt traps DN25 , NP6 (R1"). | piece | 2 |  | 1200
11 | Procurement, delivery and installation, copper pipe, of the following dimensions
| ø22x0,8 mm | m' | 8 |  | 2030
| ø28x0,8 mm | m' | 30 |  | 2340
12 | Procurement, delivery and installation,For pipe supports, brackets, additional material and tehnical gases for welding,etc, 60% is taken from the position of forks , cooper and PPR pipes , 60% from (item 3.1) | % | 0.6 |  | 86440
13 | Procurement, delivery and installation ,boiler taps for water discharge from hot water installation el. Boiler R1/2.Installation as needed with sasllCHOGY! Expert supervision. | piece | 2 |  | 750
14 | Procurement, delivery and installation of automatic venting pots R1/2. Installation as necessary with the consent of expert supervision.. | piece | 2 |  | 1200
15 | Procurement,delivery and installation of tubular sponge insulation with a vapor barrier for hot water 90/70 ° S to insulate the copper pipe network of the sanitary water preparation system .Insulation thickness 19 tt. Include material for gluing and joing.
| ø18x0,8 mm | m' | 8 |  | 480
| ø28x0,8 mm | m' | 30 |  | 550
16 | Procurement, delivery and installation of pressure gauges 0 - 6 bar. | piece | 2 |  | 2800
17 | Procurement, delivery and installation thermometar 0 - 120°C. | piece | 2 |  | 2500
7 | Various elecrical works | lump sum | 1 |  | 250000
8 | Construction works | lump sum | 1 |  | 200000
9 | Preparatory final works | lump sum | 1 |  | 50000
Total 2Sanitary water preparation system:
5. | Dismantling works
1 | Dismantling of existing heating elements, steel panel radiators, a set with fittings (approx. 15 pieces) and pipe network of black steel pipes (approx. 250 m). U this item also includes the dismantling of the connecting heating pipe DN65 from the school's boiler room, with complete insulation made of galvanized sheet steel (route approx. 50m). At at the construction site, all dismantled material, handed over to the investor. | lump sum | 1
- RECAPITULATION
Type of works EUR
2 | Sanitary water preparation system
5 | Dismantling works
68
TOTAL EUR
The tenderer is free to offer equipment/materials or similar to those provided by the bill of quantities and technical description from any manufacturer and any brand. The technical documentation does not favor any brand and any offer that is comparable to the required characteristics is acceptable.