## 5.2. Temska
5.2 - PROJECT OF A STABLE FIRE DETECTION AND ALARM SYSTEM
поз | Description works | unit measure | Quantity | EUR
1 | 2 | 3
Напомена: - У току извођења водити рачуна да се не оштете постојеће инсталације, темељи објеката, ограда и сл.
1 | Delivery, installation and commissioning of the FC510 addressable control panel, with one loop (loop length up to 2km) to which up to 250 elements can be connected, automatic detector dirt compensation, 1 conventional zone for connecting up to 30 conventional detectors, 64 fully programmable software zones, RS-485 and RS-232 interface, 16 alarm (OC) outputs, 1 controlled alarm output with the possibility of switching off, 1 programmable controlled alarm output with the possibility of switching off, 1 relay output for signaling an alarm state, 1 relay output for signaling an error, memory up to 4000 event, power supply 230V AC. | piece | 4
| The control unit has a backup battery power supply with a capacity of 2x 17A/h. Batteries in accordance with - SRPS EN 60896-21:2010 SRPS EN 60896-22:2010, SRPS N.S6.061:1989. Switchboard certified according to SRPS EN 54-2:2008. A complete set of materials and labor is paid for. | kom | 1
2 | Delivery and installation of addressable optical smoke detector FC460P, with standard 4B base, manufacturer FireClass or similar, certified SRPS EN 54-7:2008. A complete set of materials and labor is paid for. | kom | 32
3 | Испорука и монтажа адресабилног термичког детектора FC460H, са стандардним 4B подножјем, произвођач FireClass или сличан, три режима: термо-диференцијални детектор у нормалним условима, термо-маx 60ºC, термо-диференцијални са смањеном осетљивошћу. Атестиран SRPS EN 54-5:2008. Плаћа се комплет материјал и радна снага. | piece | 2
4 | Supply and installation of FC420CP-I surface mount addressable manual call point with FC420CPB mounting box, manufactured by FireClass or similar, for indoor mounting with loop isolator, resettable. Certified SRPS EN 54-11:2008, SRPS EN 54-17:20. A complete set of materials and labor is paid for. | piece | 6
5 | Delivery and installation of an alarm siren (24V, 105dB/m), manufacturer FireClass or similar. All materials and labor are paid, SRPS EN 54-2:2008, SRPS EN 54-14. | piece | 4
6 | Delivery and installation of cables J-H(St)H 2x2x0.8mm, in ribbed HF pipes ϕ16, under mortar. A complete set of materials and labor is paid for. | m | 600
7 | Delivery and installation of cables JE-H(St)H Fe180/E30 2x2x0.8mm, in ribbed HF tubes ϕ16, under mortar or on metal fireproof clamps. A complete set of materials and labor is paid for. | m | 150
8 | Delivery and installation of HF installation ribbed pipe ϕ16 mm. | m | 750
9 | Delivery and laying of cable type N2XH 3x1.5mm2 for powering the PP switchboard of the switchboard on the ground floor. A complete set of materials and labor is paid for. | m | 30
10 | Fine assembly, putting the system into operation, performing a functional test and issuing a report on the functionality of the system, as well as documents on the first control in accordance with current regulations. Training of users, issuance of certificates, delivery of the project of the completed facility. | lump sum | 1
RE CAPITULATION
Description of works
5.2 | PROJECT OF A STABLE FIRE DETECTION AND ALARM SYSTEM
68
The tenderer is free to offer equipment/materials or similar to those provided by the bill of quantities and technical description from any manufacturer and any brand. The technical documentation does not favor any brand and any offer that is comparable to the required characteristics is acceptable.
У Пироту
| Март 2024.г. | Дражен Малбаша, дипл.инг.ел.