## tender
4.1.6.2 Bill of quantity
Each point of this scope includes the delivery of the main and the procurement and delivery of all auxiliary, necessary materials, i.e. all necessary works (and what is not explicitly stated) in order for the installation to be done in accordance with all standards and regulations and for it to function smoothly.
The offer includes insurance of the construction site (workers, bystanders, materials) with an authorized insurance company, as well as securing the construction site, workers and bystanders - by applying appropriate protective measures; fencing, signaling, etc.
During the warranty period, which is not shorter than 3 years, the contractor is obliged to replace any part of the equipment that proves to be defective at his own expense and within the period determined by the Investor. The warranty period begins on the day of connection to the network
Payment will be made exclusively on the basis of the actually performed works (installed equipment and performed scope of works).
Descriptions in the bill of lading have priority over the text given in the technical description.
If "suitable equipment" is offered, the bidder is obliged to enter his offered type of equipment and manufacturer for all positions of the bill of quantities where this is requested. In that case, it is mandatory to attach a photocopy of the catalog representation of one or more elements that replace the equipment of the specified type with all functional and technical characteristics. If nothing is entered, it is assumed that the already mentioned equipment is offered.
It is the bidder's obligation to enter the types of equipment offered and the manufacturer in places where the description does not specify the type and manufacturer. Here too, it is mandatory to attach a photocopy of the catalog representation of one or more elements that replace the required equipment.
All lamps in the offer should be from a reputable manufacturer. All offered lamps should have the same or similar characteristics as the specified types of lamps. If the type of lamp is changed by the offer, it is necessary to submit complete technical documentation on the basis of which it can be determined that the offered lamp corresponds to the designed one. If the type offered is different from the one provided for in this tender, the bidder is obliged to submit the calculations made in the Dialux or Relux software package to the Investor when submitting his technical solution.
поз | Description | unit of measure | quant | EUR
Note:
Each position of the pre-measurement must include delivery, transport and assembly, connection as necessary, grounding, and bringing it to a state of full functionality.
A | ELECTRICAL INSTALLATIONS - EXTERNAL DISTRIBUTION
1. | Geometric marking of the route of the cable trench. The protocol is submitted to the Investor on paper at the very beginning of the works. Calculation per length meter of the route of all cable trenches. Set with graphic and tabular specification of excavation areas (type, location and quantities). | m | 320
2. | Control manual excavation, so-called. "slicing", width 0.4m, length 2m, depth up to 1.5m, in order to accurately determine the position of installations | complete | 2
3. | Mechanical (and, if necessary, manual) excavation of a 0.9 m deep trench in the green area, under the footpaths and parking lot, i.e. 1.4 m under the road; exceptionally in some places in agreement with the supervisory authority - depth as needed, in land of category III and IV. A set with backfilling and compaction in layers no thicker than 20 cm, obtaining a certificate of soil compaction (compaction in accordance with the purpose of the surface) and removal of excess soil. A trench is filled with sand under the footpath, parking lot and road. Calculation per meter of excavation. | m | 320
4. | Breaking asphalt (concrete) surfaces and after laying the cable, returning them to a technically correct condition | m² | 1
5. | Laying the cable in the excavated trench freely and in plastic protective pipes (the offered price does not include excavation and backfilling). The method of laying the cable is as follows: in the trench in the green area above the cable, fine earth is poured in a layer 20 cm thick, then earth from the excavation, plastic shields are laid 10 cm above the cables. At a depth of 0.4 cm from the level, a tape is laid to warn of the presence of the cable. Kit with cutting and marking of cable ends at the point of each connection in distribution cabinets. Calculation per long meter of laid cable.
5.1. | Delivery and laying of power cable line type N2XH-J 4x70mm2. The cable is laid from the cabinet of the measuring point (OMM) to the main distribution cabinet (GRO). The cable is laid in the trench, through protective HDPE pipes, fi 110 mm. The position includes the delivery of the necessary material and the connection of the cable at both ends. | m | 20
5.2. | Delivery and laying of cable line N2XH-J 5x10 mm2. The cable is laid from the main distribution cabinet (GRO), to the external lighting distribution cabinets (RO- SO), the distribution cabinet of the workshop (RO - Workshop), the distribution cabinet of the external VRF air conditioning unit (RO - air conditioning). The cable is laid in the trench through protective HDPE pipes, fi 50 mm. The position also includes the delivery of the necessary material and the connection of the cable at both ends. The position includes the total length of all cable lines of the specified type. | m | 220
5.3. | Delivery and laying of power cable line N2XH-J 5x4 mm2. The cable is laid from the main distribution cabinet (GRO) to the external connection points of the consumers within the water supply and sewage system (RO - PPOV - distribution cabinet of the waste water treatment plant). The cable is laid in the trench through protective HDPE pipes, fi 50 mm. The position includes the delivery of the necessary material and the connection of the cable at both ends. | m | 110
6. | Placement of cable markings of the route of cable lines, according to the project and the needs of the terrain. | complete | 1
| Examination of cables, other conductors and connections. Obtaining verification reports from the competent institution. | complete | 1
7. | Delivery and installation of a typical, polyester measuring cabinet (OMM) for a semi-indirect measuring group, on a concrete base, with a built-in three-pole base and 160A fuses, in accordance with the Design and Connection Conditions of EPS Elektrodistribucija Srbije. A three-phase semi-indirect measuring group will be installed in the cabinet, with an integrated timer, and current measuring transformers with a transmission ratio of 150/5A will be installed on the supply line before the meter. | piece | 1
8. | Recording the route of laid cables, protective pipes, the position of distribution cabinets with the creation of a cadastre of the completed state. The recording is handed over to the investor at the end of the works - before the finished situation is created, in paper and digital form on CD in ACAD and DWG format (with a table of absolute coordinates, as well as the breaking points of the cable route on the KAT-KOM substrates). This recording is the basis for the final calculation. Calculation per long meter of cable route. | m | 320
TOTAL А:
Б | INTERNAL ELECTRICAL INSTALLATIONS
Б.0. | Dismantling of the existing power installation and equipment. | complete | 1
Б.1 | DISTRIBUTION CABINETS
Note: In the descriptions, the approximate dimensions of the switchboard housing are given. Exact dimensions to be defined after working out the workshop documentation. The position includes the delivery, assembly and connection of distribution cabinets.
1. | GRO - Main distribution cabinet - compact cabinet with approximate dimensions 1800x1200x320, IP 65, type PLA "Himel-Schneider Electric". Access to the equipment is provided through a door that can be locked with a lock type E10K - half cylinder (in two points). Equipment equivalent to the "Schneider Electric" production program is installed in the cabinet. The wardrobe is equipped with:
Circuit breaker, ComPacT NSX160F, 36kA/415VAC, 3P, MicroLogic 2.2 protection unit 160A, manufactured by "Schneider Electric", or equivalent. - Distribution block, modular, for DIN-rail mounting, In=160A, 4p, Ipk/60ms=10kA minimum, equivalent to type LGY416048, manufactured by Schneider Electric, 1 pc. -Miniature automatic switch, In=63A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74163, manufactured by Schneider Electric, 3 pcs. -Miniature automatic switch, In=40A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74140, manufactured by Schneider Electric, 3 pcs. -Miniature automatic switch, In=32A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74132, manufactured by Schneider Electric, 3 pcs. -Miniature automatic switch, In=25A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74125, manufactured by Schneider Electric, 42 pcs. -Miniature automatic switch, In=6A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74106, manufactured by Schneider Electric, 1 pc.
| A set of installed, connected and marked equipment according to the cabinet scheme from the graphic documentation. On the lower side of the cabinet of the Pg cable entry, on the door of the cabinet prescribed markings: name of the cabinet, applied method of protection against electric shock. In the cabinet, place a pocket for documentation and the cabinet scheme, other necessary material for cabinet assembly and completion: DIN-rails, channels, conductors, sleeves, feet, row clamps, element labels, cabinet label, laces, feet, other small material necessary for planning , introduction and connection of input/output cables, testing and commissioning. | complete | 1
2. | RO - Ground floor - Supply, delivery and installation of a compact cabinet with the following characteristics: - degree of protection IP55 in accordance with EN 60529; -guides on the upper side of the cabinet; - twice pickled 1.5 mm thick sheet, plasticized; - opening the door up to an angle of 120°; - orientation dimensions 800x550x210mm; -type KB 2/5, manufactured by "Evrotehn", or equivalent. The wardrobe is equipped with:
Main disconnector, In=63A, 3p, 0-1, for DIN-rail mounting, equivalent to type VVD3, manufactured by Schneider Electric, 1 pc. - Differential current protective device, type AC, In=63A, 4p, Id=300mA, type ID K, cat. number A9Z06463, manufacturer "Schneider Electric", or equivalent, 1 pc. - Distribution block, modular, for DIN-rail mounting, In=100A, 3p (or 4p), Ipk/60ms=10kA minimum, equivalent to type LGY410028, manufactured by Schneider Electric, 1 pc. -Miniature automatic switch, In=16A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74116, manufactured by Schneider Electric, 30 pcs. -Miniature automatic switch, In=10A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74110, manufactured by Schneider Electric, 19 pcs.
| A set of installed, connected and marked equipment according to the cabinet scheme from the graphic documentation. On the lower side of the cabinet of the Pg cable entry, on the door of the cabinet prescribed markings: name of the cabinet, applied method of protection against electric shock. Place a pocket in the cabinet for documentation and the cabinet scheme, other necessary material for cabinet assembly and completion: DIN-rails, channels, conductors, sleeves, feet, row clamps, element labels, cabinet labels, laces, feet, other small material, necessary for planning, introduction and connection of input/output cables, testing and commissioning. | complete | 1
3. | RO- Basement - Delivery, installation and connection of built-in switchboard made of self-extinguishing plastic, 1x12 modules, with doors, equipped with N and PE busbars. The switchboard contains the following equipment: -ZUDS, 4p, 25A, 0.5A, 1 piece; - Miniature circuit breaker, nominal current 16A, response characteristics C, breaking capacity (Icn, according to EN/IEC 60898-1) 6kA, 1p, 4 pieces; -Miniature protective switch, nominal current 10A, response characteristics C, breaking capacity (Icn, according to EN/IEC 60898-1) 6kA, 1p, 4 pieces; -Installation and connection of all other necessary material: DIN-rail, channel, conductor, sleeve, foot, element label, cabinet label, ties, feet, other small material, necessary for planning, introduction and connection of input/output cables, testing and commissioning into work. | complete | 1
4. | RT-1 - Delivery, installation and connection of built-in switchboards (RT-A12, RT-A13, RT-A14, RT-A15, RT-A16, RT-A17) made of self-extinguishing plastic, 2x12 modules, with doors, equipped with busbars N and PE. The RT has the following equipment: -ZUDS, 4p, 25A, 0.5A, 1 piece; -ZUDS, 2p, 16A, 0.03A, 1 piece; - Miniature circuit breaker, rated current 16A, response characteristics C, breaking capacity (Icn, according to EN/IEC 60898-1) 6kA, 1p, 10 pieces; - Miniature circuit breaker, rated current 10A, response characteristics C, breaking capacity (Icn, according to EN/IEC 60898-1) 6kA, 1p, 6 pieces; -Installation and connection of all other necessary material: DIN-rail, channel, conductor, sleeve, foot, element label, cabinet label, ties, feet, other small material, necessary for planning, introduction and connection of input/output cables, testing and commissioning into work. | complete | 6
5. | RT-2 - Delivery, installation and connection of built-in switchboard made of self-extinguishing plastic, 2x18 modules, with doors, equipped with N and PE busbars. The RT-A10 features the following equipment: -ZUDS, 4p, 25A, 0.5A, 1 piece; -ZUDS, 2p, 16A, 0.03A, 2 pieces; -Miniature protective switch, nominal current 16A, response characteristics C, breaking capacity (Icn, according to EN/IEC 60898-1) 6kA, 1p, 16 pieces; -Miniature protective switch, nominal current 10A, response characteristics C, breaking capacity (Icn, according to EN/IEC 60898-1) 6kA, 1p, 16 pieces; -Installation and connection of all other necessary material: DIN-rail, channel, conductor, sleeve, foot, element label, cabinet label, ties, feet, other small material, necessary for planning, introduction and connection of input/output cables, testing and commissioning into work. | complete. | 1
6. | RO- Workshop - Delivery and assembly of a compact cabinet with the following characteristics: - degree of protection IP55 in accordance with EN 60529; -guides on the upper side of the cabinet; - twice pickled 1.5 mm thick sheet, plasticized; - opening the door up to an angle of 120°; - orientation dimensions 800x550x210mm; -type KB 2/5, manufactured by "Evrotehn", or equivalent. The wardrobe is equipped with:
Main disconnector, In=40A, 3p, 0-1, for DIN-rail mounting, equivalent to type VVD2, manufactured by Schneider Electric, 1 pc. - Differential current protection device, type AC, In=40A, 4p, Id=300mA, type ID K, cat. number A9Z06440, manufacturer "Schneider Electric", or equivalent, 1 pc. - Distribution block, modular, for DIN-rail mounting, In=100A, 3p (or 4p), Ipk/60ms=10kA minimum, equivalent to type LGY410028, manufactured by Schneider Electric, 1 pc. -Miniature automatic switch, In=16A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74116, manufactured by Schneider Electric, 25 pcs. -Miniature automatic switch, In=10A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74110, manufactured by Schneider Electric, 10 pcs.
| A set of installed, connected and marked equipment according to the cabinet scheme from the graphic documentation. On the lower side of the cabinet of the Pg cable entry, on the door of the cabinet prescribed markings: name of the cabinet, applied method of protection against electric shock. Place a pocket in the cabinet for documentation and the cabinet scheme, other necessary material for cabinet assembly and completion: DIN-rails, channels, conductors, sleeves, feet, row clamps, element labels, cabinet labels, laces, feet, other small material, necessary for planning, introduction and connection of input/output cables, testing and commissioning | complete | 1
УКУПНО Б1:
Б.2 | INTERNAL DISTRIBUTION OF ELECTRICAL INSTALLATIONS FOR GENERAL PURPOSE CONNECTORS, FIXED OUTLETS AND LIGHTING
1. | Supply of necessary material and installation of fire resistant cable tray type SKS 610FS/6056105 E90, OBO Bettermann or similar, with knocked down edges, without cover, depth 60 mm. The position includes the delivery and installation of typical wall and ceiling supports, as well as elements for changing the direction with the same fire characteristics and in accordance with DIN 4102-12.
1.1. | Perforated cable tray 200 mm wide, without cover. | m | 50
1.2. | Perforated cable tray 100 mm wide, without cover. | m | 80
2. | Supply and installation of fire-resistant cable rack cover E90, OBO Bettermann or equivalent, in accordance with DIN 4102-12.
2.1. | Cable rack cover with a width of 200 mm. | m | 50
2.2. | Cable rack cover with a width of 100 mm. | m | 80
| Delivery of the necessary material and installation of ribbed HDPE pipes, fi 50 in the floor distribution. | m | 15
3. | Delivery of the necessary material and installation of hard installation PVC smooth pipes, fi 29, with wall brackets. | m | 150
4. | Delivery and installation of installation PVC flexible pipes, fi 29 - mechanically reinforced. | m | 90
5. | Delivery of the necessary material and installation of the distribution cabinet power supply of the RO-ground floor, with cable type N2XH-J 5x16 mm2. The position includes making cable terminations and connecting the installation at the connected end of the consumption. The cable is laid on cable racks, through protective pipes and on the wall, under the plaster. | m | 5
6. | Delivery of the necessary material and installation of the power supply of the distribution cabinet of the basement, with a cable type N2XH-J 5x10 mm2. The position includes making cable terminations and connecting the installation at the connected end of the consumption. The cable is laid on cable racks, through protective pipes and on the wall, under the plaster. | m | 15
7. | Delivery of the necessary material and installation of the power supply of the distribution boards of the rooms, with a cable type N2XH-J 5x4 mm2. The position includes making cable terminations and connecting the installation at the connected end of the consumption. The cable is laid on cable racks, through protective pipes and on the wall, under the plaster. | m | 120
8. | Delivery of the necessary material and installation of the power supply of three-phase sockets 16A and fixed connection points, with cable type N2XH-J 5x2.5 mm2. The position includes making cable terminations and connecting the installation at the connected end of the consumption. The cable is laid on cable racks, through protective pipes and on the wall, under the plaster. | m | 180
9. | Delivery of the necessary material and installation of the power supply of single-phase 16A sockets and fixed connection points, with cable type N2XH-J 3x2.5 mm2. The position includes making cable terminations and connecting the installation at the connected end of the consumption. The cable is laid on cable racks, through protective pipes and on the wall under the plaster. | m | 250
10. | Delivery of the necessary material and construction of the installation of the power supply of lighting points and fixed outlets, with cable type N2XH-J 3x1.5 mm2. The position includes making cable terminations and connecting the installation at the connected end of the consumption. The cable is laid on cable racks, through protective pipes and on the wall under the plaster. | m | 450
total Б.2 :
Б.3 | installation of internal potential equalization
1. | Delivery and installation of the main busbar box for potential equalization GSIP. | piece | 1
2. | Delivery of the necessary material and creation of potential equalization from GSIP to the PE bus in GRO, with a conductor type N2XH-J 1x70 mm2. Kit with all necessary material. | complete | 1
3. | Delivery of the necessary material and creation of equalization of the potential of all metal masses. Make connections from GSIP to cable racks, plumbing pipes, heating, ventilation ducts and other metal masses, with a conductor type N2XH-J 1x16mm2. Kit with all necessary material. | complete | 1
4. | Delivery of the necessary material and creation of the installation of equalization of potential in wet churros. Connection of the bus in the PS-49 box and the metal masses with a cable type N2XH-J 1x6 mm2. The cable is laid in the wall or floor through a PVC ribbed pipe fi 16mm. Complete with all necessary materials. | complete | 8
5. | Delivery of the necessary material and installation of equalization of the potential of metal masses in the technical rooms of machine installations. Make bridges of insulated flange joints on heating pipes, ventilation ducts and connect them with SIP conductor N2XH-J 1x6 mm2. Bridging should be done with a copper braid of 6mm2 section with terminal feet at the ends. All set. | complete | 1
6. | Delivery of the necessary material and installation of equalization of the potential of metal masses in the technical rooms of machine installations. Make bridges of insulated flange joints on heating pipes, ventilation ducts and connect them with SIP conductor N2XH-J 1x6 mm2. Bridging should be done with a copper braid of 6mm2 section with terminal feet at the ends. All set. | piece | 8
TOTAL Б.3 :
Б.4 | INSTALLATION EQUIPMENT AND ACCESSORIES
Procurement, delivery and installation of installation equipment. The specified equipment from the Aling, Schrack, Legrand or corresponding product range, modular sockets and switches, mask PVC white.
1. | Built-in switch 230V, 10A, white, single-pole, complete with installation box 60 mm, installation in a plaster wall. | complete | 13
2. | Built-in switch 230V, 10A, white, serial, complete with installation box 60 mm, installation in a plaster wall. | piece | 10
3. | Built-in switch 230V, 10A, white, alternating, complete with installation box 60 mm, installation in a plaster wall. | piece | 6
4. | Built-in single-phase socket with spring-loaded child protection, 230V, 16A, white, installation in the wall. | piece | 46
5. | Built-in single-phase socket 230V, 16A, white, installation in the wall. | piece | 6
6. | Built-in double single-phase socket 230V, 16A, white, installation in the wall. | piece | 4
7. | Built-in single-phase socket with cover 230V, 16A, white, installation in the wall | piece | 17
8. | Surface-mounted single-phase socket with cover 230V, 16A, IP44, white, wall mounting. | piece | 1
9. | Built-in three-phase socket 400V, 16A, white, installation in the wall. | piece | 3
10. | Surface three-phase socket with cover 400V, 16A, IP44, white, wall mounting. | piece | 5
TOTAL .4 :
Б.5 | LAMPS - INTERIOR LIGHTING
Delivery and installation of lamps for internal functional and safety lighting. Luminaires are installed in everything according to the project and in a manner determined by the construction of the luminaire or by means of specified supporting accessories. The position of the lamps also includes a structure for hanging the lamps, which is solved on the spot. The power supply voltage of the lamps is 220-240V, 50Hz. The lamp includes light sources, and all auxiliary material for the operation of the lamp and their installation (holders, hangers, cables)
1. | S1 - Lamp with LED source for wall mounting in rooms, type MONO white 7808 Nowodvorski, or suitable. | piece | 42
enter the type of lamp offered:
enter the name of the manufacturer:
2. | С2 - Recessed downlighter type of wide-beam optics, made in LED technology, intended for installation in a suspended monolithic or Armstrong ceiling with an outer diameter of 215 mm, and a cut-out diameter of 200 mm, while the depth of the lamp is extremely small, 28 mm. The housing of the lamp is made of aluminum painted white, while the reflector of the lamp and the optical block are made of polycarbonate. The degree of mechanical protection is IP 44, and the impact resistance is IK 02, while the current class is II. The lamp is delivered complete with LED modules with light color 4000 K, electronic ballasts and color reproduction index Ra 80. Efficiency min 100 lm/W, total flux of the system is 2100 lm. The total power of the system is 21W. The time for which the luminous flux drops to 70% of the initial flux is 50,000 hours. A maximum of five percent of the drivers will be defective after 50,000 hours. The temperature range of lamp operation is from 0 to +35 degrees Celsius. The lamp has a mass of 0.52 kg. The lamp should comply with the European directives that apply to products, and have a CE mark.
| Lamp type Philips CoreLine SlimDownlight DN145B LED20S/840 PSU II WH, manufactured by Signify, or suitable. | piece | 27
enter the type of lamp offered:
enter the name of the manufacturer:
3. | С3 Recessed lamp made in LED technology with two LED sources, intended for installation in a suspended ceiling, for lighting interior rooms. The housing of the lamp is made of steel, while the optics and reflector of the lamp are made of polycarbonate. Angle of light emission 100 degrees. The degree of mechanical protection is IP 44, impact resistance is IK 03, current class I. The lamp has a push-in connector for easier installation, without opening the lamp. Color uniformity SDCM (0.43,0.40) less than or equal to 3. The lamp is supplied complete with LED modules with light color 3000 K, electronic ballasts and color rendering index Ra greater than 80. Lamp efficiency min 130 lm/W. The lamp has two switches, the combination of which adjusts the amount of light given by the lamp. It is possible to choose three lumen packages 2,800, 3,400 and 4,000 lm (choose 2,800 lm). The total power of the system would then be 22, 26 and 31W. The time for which the luminous flux drops to 85% of the initial flux is 50,000 hours. A maximum of five percent of the drivers will be defective after 50,000 hours. Designed for frequent switching on. The lamp has a mass of 3.4 kg. The lamp should comply with the European standard on safe and proper operation, and have the ENEC mark.
| Lamp type Philips CoreLine Recessed RC136B 28S_34S_40S/830 PSU W60L60 NOC, manufactured by Signify or suitable | piece | 29
enter the type of lamp offered:
enter the name of the manufacturer:
4. | С4 - Recessed downlighter type lamp made with a 3D printer with wide beam optics, made in LED technology, intended for installation in a suspended monolithic or Armstrong ceiling with an outer diameter of 400 mm, while the depth of the lamp is 82 mm. The UGR factor is less than or equal to 19. The degree of mechanical protection is IP 20, and the impact resistance is IK 04. The lamp is supplied complete with LD modules with light color 4000 K, electronic ballasts and color reproduction index Ra 90. Efficiency min 122 lm /W, the total flux of the system is 1900 lm. The total power of the system is 15.4 W. The temperature range of the lamps is from +10 to +35 ºC. The lamp should comply with the European directives that apply to products, and have a CE mark.
| Lamp type Philips Essential Series RMR19S940PSUOCWH401NNNNN, manufactured by Signify, or equivalent. | piece | 12
enter the type of lamp offered:
enter the name of the manufacturer:
5. | С5 - Hanging lamp in the shape of a thin cylinder made by a 3D printer with wide beam optics, made in LED technology, intended for mounting on a ceiling with an outer diameter of 390 mm, while the depth of the lamp is 85 mm with a 3D texture on the lamp housing. The maximum length of hangers is 2800 mm. The UGR factor is less than or equal to 19. The degree of mechanical protection is IP 20, and the impact resistance is IK 04. The lamp is supplied complete with LED modules with light color 4000 K, electronic ballasts and color reproduction index Ra 90. Efficiency min 122 lm /W, the total flux of the system is 1900 lm. The total power of the system is 15.4W. The temperature range of lamp operation is from +10 to +35 degrees Celsius. The lamp should comply with the European directives that apply to products, and have a CE mark.
| Lamp type Philips Essential Series BRMP19S940PSUOCWH401T305WHNNN, manufactured by Signify, or suitable. | piece | 5
enter the type of lamp offered:
enter the name of the manufacturer:
6. | С6 - Hanging narrow linear lamp made in LED technology with LED light sources, designed for mounting on the ceiling, for corridor lighting (UGR factor less than or equal to 19) dimensions 70x1127mm. The housing of the lamp is made of aluminum, while the optics and protector of the lamp are made of polycarbonate. The lamp reflector is made of steel. The light emission angle is 74 degrees. The degree of mechanical protection is IP20, impact resistance is IK 02, current class I. The lamp has a push-in connector for easier installation, without opening the lamps. Color uniformity SDCM less than 3. The lamp is supplied complete with LED modules with light color 4000K, electronic ballasts and color reproduction index Ra greater than 80. Lamp efficiency min 132 lm/W. The total flux of the system is 1,800 lm. The maximum power of the system is 13.6W. The time for which the luminous flux drops to 90% of the initial flux is 50,000 hours. A maximum of five percent of the drivers will be defective after 50,000 hours. The lamp has a mass of 2.75 kg. The lamp should comply with the European standard on safe and proper operation, and have the ENEC mark. The lamp must comply with the European directives that apply to products, and must have the CE mark. Note: the lamp is mounted in accordance with the architectural construction solution of the suspended ceiling.
| Lamp type Philips KeyLine SM350C 18S/840 PSU PCS L1200 WH, manufactured by Signify or suitable. | piece | 15
уписати тип понуђене светиљке:
enter the name of the manufacturer:
7. | С7 - Surface mounted narrow line lamp made in LED technology with LED light sources, intended for mounting on the ceiling, for lighting classrooms and offices (UGR factor less than or equal to 19) dimensions 70x1127mm. The housing of the lamp is made of aluminum, while the optics and protector of the lamp are made of polycarbonate. The lamp reflector is made of steel. The light emission angle is 74 degrees. The degree of mechanical protection is IP20, impact resistance is IK 02, current class I. The lamp has a push-in connector for easier installation, without opening the lamps. Color uniformity SDCM less than 3. The lamp is supplied complete with LED modules with light color 4000 K, electronic ballasts and color reproduction index Ra greater than 80. Lamp efficiency min 132 lm/W. The total flux of the system is 1,800 lm. The maximum power of the system is 13.6W. The time for which the luminous flux drops to 90% of the initial flux is 50,000 hours. A maximum of five percent of the drivers will be defective after 50,000 hours. The lamp has a mass of 2.75 kg. The lamp should comply with the European standard on safe and proper operation, and have the ENEC mark. The lamp must comply with the European directives that apply to products, and must have the CE mark.
| Lamp type Philips KeyLine SM350C 18S/840 PSU PCS L1200 WH, manufactured by Signify, or suitable. | piece | 5
enter the type of lamp offered:
enter the name of the manufacturer:
8. | С8 - Surface-mounted waterproof wide-beam lamp with one light source, made in LED technology with rounded ends, intended for mounting on the ceiling, dimensions 1215x80 mm. The housing of the lamp is made of polycarbonate, painted in gray. Optical block and protector also made of polycarbonate. The degree of mechanical protection is IP 65, the impact resistance is IK 08, while the current class is I. Color uniformity SDCM (0.38,0.38) ≤3. The lamp is supplied complete with LED modules with a light color of 4000 K, electronic ballasts and a color reproduction index Ra greater than 80. Lamp efficiency min 140 lm/W, total initial flux of the system is 4000 lm. The total maximum power of the system is 28.6W. The time for which the luminous flux drops to 85% of the initial flux is 50,000 hours. A maximum of five percent of the drivers will be defective after 50,000 hours. Designed for frequent switching on. The temperature range of lamp operation is from -20 to +40 ºC. The lamp has a mass of 1.33 kg. The lamp should comply with the European standard on safe and proper operation, and have the ENEC mark. The lamp must comply with the European directives that apply to products, and must have the CE mark.
| Lamp type Philips CoreLine Waterproof WT120C G2 LED40S/840 PSU L1200, manufactured by Signify. or appropriate | piece | 4
enter the type of lamp offered:
enter the name of the manufacturer:
9. | С9 - Surface-mounted waterproof wide-beam lamp with one light source, made in LED technology with a rectangular cross-section, intended for mounting on the ceiling, dimensions 1248x96x68 mm. The housing of the lamp is made of polycarbonate, painted in gray. Optical block and protector also made of polycarbonate. The degree of mechanical protection is IP66, the impact resistance is IK 08, while the current class is I. Color uniformity SDCM (0.38,0.38) ≤3. The lamp is supplied complete with LED modules with a light color of 4000 K, electronic ballasts and a color reproduction index Ra greater than 80. The efficiency of the lamp min 160 lm/W, the total initial flux of the system is 6400 lm. The total maximum power of the system is 40W. The time for which the luminous flux drops to 95% of the initial flux is 50,000 hours. A maximum of five percent of the drivers will be defective after 50,000 hours. Designed for frequent switching on. The temperature range of lamp operation is from -25 to +45 ºC. The lamp has a mass of 2.8 kg. The lamp should comply with the European standard on safe and proper operation, and have the ENEC mark. The lamp should comply with the European directives that apply to products, and have a CE mark.
| Lamp type Philips Pacific LED Gen5 WT490C 64S/840 PSU WB PI5 L1200, manufactured by Signify, or equivalent. | piece | 4
enter the type of lamp offered:
enter the name of the manufacturer:
10. | С10 - Lamp for urban lighting with asymmetric wide-beam optics (DW) in the shape of a rounded cone, total power 46.4W, total initial luminous flux of the complete lamp 6725 lm, LOR 85% and light efficiency minimum 145lm/W. Neutral white (NW) light color temperature 4000K, color reproduction index Ra greater than 70. Durability of the LED source at least 100,000 hours, provided that the flux does not drop to less than 97% of the initial one. The housing of the lamp is made of aluminum alloy cast under pressure and painted with an electrostatic process, in gray color. Protector and optics made of polycarbonate. Integrated programmable DALI LED driver. The optics of the lamp are symmetrical. Complete lamp in the degree of mechanical protection IP66. Impact resistance IK11. Supply voltage 120-277V. Degree of protection against electric shock minimum in class I. Overvoltage protection is 10 kV. Operating temperature from -40 degrees to +50 ºC. The assembly is done on the top of the pole (fi 62 mm), axially symmetrical in relation to the pole, without additional accessories. Lamp equipped with bayonet connector and M20 inlet. Fixing screws must be corrosion resistant. The lamp has a service tag, which allows with the use of an application on a mobile device, a detailed description of the lamp, instructions for installation and maintenance, registration of the lamp, a list of service parts, programming of the driver on the ground,... The lamp should comply with the European standard on safe and proper operation , to have the ENEC mark. The lamp should comply with the European directives that apply to products, to have the CE mark.
| Светиљка типа Philips CityCharm Fluid BDS492 LED80/740 PSD I DW GRB GR 60 SRG10, произвођача Signify, или одговарајућа. | piece | 4
enter the type of lamp offered:
enter the name of the manufacturer:
11. | C11-Procurement, delivery and installation of facade lamps for outdoor use, equipped with a bracket for surface mounting and with the possibility of turning on both axes, with a separate driver and powerful LED sources with a total maximum power of 15W, a total minimum initial flux of the lamp of 720 lm. Minimum lamp efficiency 48lm/W. The lamp has the ability to change RGBW color via the DMX protocol. The housing and bracket are made of die-cast aluminum and powder coated. The bracket enables the adjustment of the angle of inclination. PMMC protector. The frame dimensions of the lamp are 1000x72x25 mm. The optical system provides a radiation angle of 45°. The lamp has a degree of mechanical protection IP 66, IK 6. The frame mass of the lamp is 0.857 kg. Lamp equivalent to Philips UniStrip G4 BCP386 60LED RGBWW 24V 45 L100 DMX, manufactured by Signify or equivalent. The kit consists of: BCP386 60LED RGBWW 24V 45 L100 DMX - 8 pcs. Leader Cable - 1 pc. Jumper Cable - 7 pcs. Driver - 8 pcs.
| Lamp type Philips UniStrip G4 BCP386 60LED RGBWW 24V 45 L100 DMX, manufactured by Signify, or suitable. | complete | 1
enter the type of lamp offered:
enter the name of the manufacturer:
12. | Controller SSLCTR LRC9628 IPLAYER3 EU (100-240V) | piece | 1
13. | Panel SSLCTR LRC9629 SERIAL KEYPAD | piece | 1
14. | Programming and commissioning. | piece | 1
15. | Panic lamp type SL2MNM42D3C3A Eaton, or equivalent. | piece | 19
enter the type of lamp offered:
enter the name of the manufacturer:
16. | Panic lamp type SL2MNM65D3C3A Eaton, or equivalent. | piece | 5
enter the type of lamp offered:
enter the name of the manufacturer:
17. | Motion detector ESS 10630, 360D, ceiling, max 400, adj T=5 sec-5min, IP20- SCHRACK, or suitable. | piece | 8
TOTAL Б.5 :
Б.6 | GROUNDING AND LIGHTNING ARRESTER INSTALLATIONS
| Manual/Mechanical (depending on the conditions on the ground) excavation of a trench measuring 0.2x0.8m for the laying of a strip grounding device. After laying the earthing strip, backfill the trench with earth from the excavation. Calculation per meter of route. | m | 190
| Delivery and installation of galvanized strip FeZn 25x4 mm for the production of a strip grounding device. The tape is laid directly in the ground. Interconnect with cross pieces. Cross pieces are included in the price | m | 240
| Delivery and installation of galvanized strip FeZn 25x4 mm for the production of leads from the grounding device to the downcomers of lightning protection. The average length of the extract is 5.5 m. The tape is laid partly through the ground and partly on the facade under the mechanical protection. | complete | 14
| Delivery and installation of galvanized strip FeZn 25x4 mm for making the outlet from the grounding device to the gutter verticals. The average length of the extract is 4.5 m. | complete | 8
| Delivery and installation of a galvanized strip FeZn 25x4 mm for the creation of the outlet from the grounding device to the main buses for potential equalization. The average length of the outlet strip is 5 m. Kit with cross piece. | complete | 1
| Delivery and installation of copper wire Ø8 mm full cross-section for making down lines of lightning arrester installation. The wire is placed on the facade of the building on typical supports. | complete | 1
| Procurement, delivery and installation of copper wire Ø8 mm full section for the production of the receiving system of the lightning rod installation. The wire is placed on typical supports for the roof. | complete | 1
| Small installation material needed for making a lightning rod installation | complete | 1
TOTAL Б.6 :
Ц | EXTERIOR LIGHTING - FUNCTIONAL YARD LIGHTING AND SPORT FIELD LIGHTING
18. | Freestanding polyester public lighting cabinet of approximate dimensions 1000x500x320, IP 65, with canopy, inlets, own polyester foundation, supporting sheet metal plate, equivalent to PLA "Himel-Schneider Electric" type. Access to the equipment is provided through a door that can be locked with a type lock E10 K - half cylinder (in two points). Equipment equivalent to the "Schneider Electric" production program is installed in the cabinet. The wardrobe is equipped with:
Distribution block, modular, for DIN-rail mounting, In=100A, 3p (or 4p), Ipk/60ms=10kA minimum, equivalent to type LGY410028, manufactured by Schneider Electric, 1 pc. - Device for automatic control of lighting on and off, digital, 4-channel Astro and annual timer Schrack 4TE, 1 pc. -Main disconnector, In=40A, 3p, 0-1, for DIN-rail mounting, equivalent to type VVD2, manufactured by Schneider Electric, 1 pc - Modular contactor, In=25A, 3p, control voltage 230Vac, equivalent to type iCT, manufactured by Schneider Electric, 5 pcs. -Selection switch, modular, for DIN-rail mounting, 1p, three-position, 1-0-2 (manual-off-automatic), equivalent to type A9E18073, manufactured by Schneider Electric, 5 pcs. -Miniature automatic switch, In=40A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74140, manufactured by Schneider Electric, 3 pcs. -Miniature automatic switch, In=10A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74110, manufactured by Schneider Electric, 18 pcs. -Miniature automatic switch, In=6A, 1p, C, breaking capacity (Icu) according to IEC/EN 60947-2 10kA, equivalent to type A9F74106, manufactured by Schneider Electric, 4 pcs.
| A set of installed, connected and marked equipment according to the cabinet scheme from the graphic documentation. On the lower side of the cabinet of the Pg cable entry, on the door of the cabinet prescribed markings: name of the cabinet, applied method of protection against electric shock. In the cabinet, place a pocket for documentation and the cabinet scheme, other necessary material for cabinet assembly and completion: DIN-rails, channels, conductors, sleeves, feet, regular clamps, element markings, cabinet markings, ties, feet, other small material necessary for planning, introduction and connection of input/output cables, testing and commissioning work. | piece | 1
RECAPITULATION
A | ELECTRICAL INSTALLATIONS - EXTERNAL DISTRIBUTION
Б.0 | DISMANTLING OF EXISTING EE INSTALLATION AND EQUIPMENT
Б.1 | DISTRIBUTION CABINETS
Б.2 | INTERNAL DISTRIBUTION OF ELECTRICAL INSTALLATIONS FOR GENERAL PURPOSE CONNECTORS, FIXED OUTLETS AND LIGHTING
Б3 | NSTALLATION OF INTERNAL EQUALIZATION
Б4 | INSTALLATION EQUIPMENT AND ACCESSORIES
Б.5 | AMPS - INTERIOR LIGHTING
Б.6 | GROUNDING AND LIGHTNING ARRESTER INSTALLATIONS
Ц | EXTERIOR LIGHTING - FUNCTIONAL YARD LIGHTING AND SPORT FIELD LIGHTING
Pancevo
March 2023.године
The tenderer is free to offer equipment/materials or similar to those provided by the bill of quantities and technical description from any manufacturer and any brand. The technical documentation does not favor any brand and any offer that is comparable to the required characteristics is acceptable
Зорица Нинић Ступар, дипл. инж. ел.
Лиценца број: 350 2661 03